## Instructions
BBV51917 ATV12 - Communication Parameters - 1.4IE05
DANGER
UNINTENDED EQUIPMENT OPERATION •Read and understand this document, the User Manual and Modbus Manual before installing or operating the Altivar 12 drive. •Any changes made to the parameter settings must be performed by qualified personnel. Failure to follow these instructions will result in death or serious injury.
WARNING
LOSS OF CONTROL •The designer of any control scheme must - consider the potential failure modes of control paths and, for certain critical control functions, - provide a means to achieve a safe state during and after a path failure. Examples of critical control functions are emergency stop and overtravel stop. •Separate or redundant control paths must be provided for critical control functions. •System control paths may include communication links. Consideration must be given to the implications of unanticipated transmission delays or failures of the link. (see note a.) Failure to follow these instructions can result in death, serious injury, or equipment damage.
Note a.: For additional information, refer to NEMA ICS 1.1 (latest edition), “Safety Guidelines for the Application, Installation, and Maintenance of Solid State Control” and to NEMA ICS 7.1 (latest edition), “Safety Standards for Construction and Guide for Selection, Installation and Operation of Adjustable-Speed Drive Systems.”
Electrical equipment should be installed, operated, serviced, and maintained only by qualified personnel. No responsibility is assumed by Schneider Electric for any consequences arising out of the use of this material.
EXPLANATORY NOTE
This Excel file is for reference only . Refer to both the Altivar 12 User Manual and the Altivar 12 Modbus Communication Manual for full information.
This Excel file can be used to carry out searches (e.g. parameter address and format) and sort operations.
The columns include the following criteria:
Code: Language-independent, this allows a rapid search in the Altivar 12 User Manual, which includes an index of parameter codes.
Additional information can be found in the Altivar 12 Modbus Communication Manual.
Name: Parameter designation
Logic address: Address for the Modbus messaging are in decimal and hexadecimal (preceded by 16#) format.
To optimize Modbus messaging performance, two addresses are given for the control word (CMD) and the status word (ETA).
The addresses annotated "speed" are for use in rpm; the addresses annotated "frequency" are for use in Hz.
Link: For WORD type parameters, a dynamic link opens the description of a bit register or a listing. Listings are common to several parameters; only one part is valid for a given parameter. Refer to both the Altivar 12 User Manual and the Altivar 12 Modbus Communication Manual to determine the valid values. If an invalid value is written to a configuration parameter, the drive will indicate a fault [Invalid config.] (CFI).
Category: Defines the role of the parameter, for example: Command parameter, Status parameter, etc.
Access: Read and write options:
R: Read only
R/W: Read and write
R/WS: Read and write (write only possible when the drive is not in RUN mode).
It is not possible to write these parameters in "5-Operation enabled" or "6-Quick stop active" states.
If the parameter is written in the "4-Switched on" state, transition 10 to "2-Switch on disabled" is activated.
Type:
WORD (bit register): Word where each bit represents a command or a state
WORD (listing): Word where each value represents a possible choice for a configuration or state
INT: Signed integer
UINT: Unsigned integer
DINT: Signed double integer
UDINT: Unsigned double integer
Units: Physical unit and multiplier
Factory setting: Value of the parameter set at the factory.
Range: Possible values
Display: Parameter name displayed on the graphic display terminal, in square brackets [---], and parameter code displayed by the 7-segment digits on the integrated display terminal, in round brackets (---).
Menu: Indicates the menus or menus where the parameter is located. Menu name displayed on the graphic display terminal, in square brackets [---], and menu code displayed by the 7-segment digits on the integrated display terminal, in round brackets (---).
Order: Gives the initial storage order of the parameter in the file, from 1 to n. This makes it possible, after sorting operations, to put this file back in its initial order by sorting the column in ascending order.
EXPLANATORY NOTE
This Excel file is for reference only . Refer to both the Altivar 12 User Manual and the Altivar 12 Modbus Communication Manual for full information.
This Excel file can be used to carry out searches (e.g. parameter address and format) and sort operations.
The columns include the following criteria:
Code: Language-independent, this allows a rapid search in the Altivar 12 User Manual, which includes an index of parameter codes.
Additional information can be found in the Altivar 12 Modbus Communication Manual.
Name: Parameter designation
Logic address: Address for the Modbus messaging are in decimal and hexadecimal (preceded by 16#) format.
To optimize Modbus messaging performance, two addresses are given for the control word (CMD) and the status word (ETA).
The addresses annotated "speed" are for use in rpm; the addresses annotated "frequency" are for use in Hz.
Link: For WORD type parameters, a dynamic link opens the description of a bit register or a listing. Listings are common to several parameters; only one part is valid for a given parameter. Refer to both the Altivar 12 User Manual and the Altivar 12 Modbus Communication Manual to determine the valid values. If an invalid value is written to a configuration parameter, the drive will indicate a fault [Invalid config.] (CFI).
Category: Defines the role of the parameter, for example: Command parameter, Status parameter, etc.
Access: Read and write options:
R: Read only
R/W: Read and write
R/WS: Read and write (write only possible when the drive is not in RUN mode).
It is not possible to write these parameters in "5-Operation enabled" or "6-Quick stop active" states.
If the parameter is written in the "4-Switched on" state, transition 10 to "2-Switch on disabled" is activated.
Type:
WORD (bit register): Word where each bit represents a command or a state
WORD (listing): Word where each value represents a possible choice for a configuration or state
INT: Signed integer
UINT: Unsigned integer
DINT: Signed double integer
UDINT: Unsigned double integer
Units: Physical unit and multiplier
Factory setting: Value of the parameter set at the factory.
Range: Possible values
Display: Parameter name displayed on the graphic display terminal, in square brackets [---], and parameter code displayed by the 7-segment digits on the integrated display terminal, in round brackets (---).
Menu: Indicates the menus or menus where the parameter is located. Menu name displayed on the graphic display terminal, in square brackets [---], and menu code displayed by the 7-segment digits on the integrated display terminal, in round brackets (---).
Order: Gives the initial storage order of the parameter in the file, from 1 to n. This makes it possible, after sorting operations, to put this file back in its initial order by sorting the column in ascending order.

## Parameters
Code | Name | Logic address | CANopen index | INTERBUS index | DeviceNet path | Link | Category | Access | Type | Units | Factory setting | Range | Display | Menu | Order
CMD | Control word | 16#2199 = 8601 (speed) 16#2135 = 8501 (frequency) | - | - | - | CMD | Control parameters | R/W | WORD (BitString16) | - | - | - |  |  | 1
CMI | Extended control word | 16#2138 = 08504 | - | - | - | CMI | Control parameters | R/W | WORD (BitString16) | - | - | - |  |  | 2
RPR | Reset counters command | 16#0C30 = 03120 | - | - | - | RPR | Control parameters | R/W | WORD (Enumeration) | - | "NO" | - | (rPr) | (FLt-) | 3
LFRD | Speed setpoint | 16#219A = 08602 | - | - | - | - | Setpoint parameters | R/W | INT (Signed16) | 1 rpm | 0 | -32767 rpm ... 32767 rpm |  |  | 4
LFR | Frequency setpoint | 16#2136 = 08502 | - | - | - | - | Setpoint parameters | R/W | INT (Signed16) | 0.1 Hz | 0 | -3276.7 Hz ... 3276.7 Hz | (LFr) | (rEF-) (MOn-) (CtL-) | 5
PISP | PID regulator setpoint | 16#2137 = 08503 | - | - | - | - | Setpoint parameters | R/W | UINT (Unsigned16) | 0.1 % | 0 | 0 % ... 100 % |  |  | 6
AIV1 | Analog input virtual | 16#14A1 = 05281 | - | - | - | - | Setpoint parameters | R/W | INT (Signed16) | 0.1 % | 0 | 0 % ... 100 % | (AIU1) | (rEF-) (MOn-) (CtL-) | 7
ETA | Status word | 16#219B = 8603 (speed) 16#0C81 = 3201 (frequency) | - | - | - | ETA | Status parameters | R | WORD (BitString16) | - | - | - |  |  | 8
HMIS | Product status | 16#0CA8 = 03240 | - | - | - | HMIS | Status parameters | R | WORD (Enumeration) | - | "TUN" | - |  |  | 9
ETI | Extended status word | 16#0C86 = 03206 | - | - | - | ETI | Status parameters | R | WORD (BitString16) | - | - | - |  |  | 10
CRC | Active reference channel | 16#20F9 = 08441 | - | - | - | CCC | Status parameters | R | WORD (BitString16) | - | - | - |  |  | 11
CCC | Active command channel | 16#20FA = 08442 | - | - | - | CCC | Status parameters | R | WORD (BitString16) | - | - | - |  |  | 12
RFRD | Output velocity | 16#219C = 08604 | - | - | - | - | Actual values parameters | R | INT (Signed16) | 1 rpm | 0 | -32767 rpm ... 32767 rpm |  |  | 13
RFR | Estimated motor frequency (signed value) | 16#0C82 = 03202 | - | - | - | - | Actual values parameters | R | INT (Signed16) | 0.1 Hz | 0 | -500 Hz ... 500 Hz | (rFr) | (MOn-) | 14
LCR | Estimated motor current | 16#0C84 = 03204 | - | - | - | - | Actual values parameters | R | UINT (Unsigned16) | 0.1 A | 0 | 0 A ... 6553.5 A | (LCr) | (MOn-) | 15
OPR | Output power monitoring (100% = nominal motor power) | 16#0C8B = 03211 | - | - | - | - | Actual values parameters | R | INT (Signed16) | 1 % | 0 | -32767 % ... 32767 % | (OPr) | (MOn-) | 16
FRH | Frequency reference before ramp | 16#0C83 = 03203 | - | - | - | - | Reference parameters | R | INT (Signed16) | 0.1 Hz | 0 | -3276.7 Hz ... 3276.7 Hz | (FrH) | (rEF-) (MOn-) | 17
RPC | PID reference after ramp | 16#2ECE = 11982 | - | - | - | - | Reference parameters | R | UINT (Unsigned16) | 0.1 % | 0 | 0 % ... 6553.5 % | (rPC) | (rEF-) (MOn-) | 18
RPF | PID regulator feedback reference | 16#2ECD = 11981 | - | - | - | - | Reference parameters | R | UINT (Unsigned16) | 0.1 % | 0 | 0 % ... 6553.5 % | (rPF) | (MOn-) | 19
RPE | PID regulator discrepancy | 16#2ECC = 11980 | - | - | - | - | Reference parameters | R | INT (Signed16) | 0.1 % | 0 | -3276.7 % ... 3276.7 % | (rPE) | (MOn-) | 20
ULN | Main voltage (from DC bus) | 16#0C87 = 03207 | - | - | - | - | Measurement parameters | R | UINT (Unsigned16) | 1 V | 0 | 0 V ... 65535 V | (ULn) | (MOn-) | 21
THD | Drive thermal state | 16#0C89 = 03209 | - | - | - | - | Measurement parameters | R | UINT (Unsigned16) | 1 % | 0 | 0 % ... 200 % | (tHd) | (MOn-) | 22
THR | Motor thermal state | 16#259E = 09630 | - | - | - | - | Measurement parameters | R | UINT (Unsigned16) | 1 % | 0 | 0 % ... 200 % | (tHr) | (MOn-) | 23
PTH | Total drive operating time | 16#0CA1 = 03233 | - | - | - | - | Measurement parameters | R | UINT (Unsigned16) | 0.01 h | 0 | 0 h ... 655.35 h | (PtH) | (MAI-) | 24
TAC | IGBT alarm time | 16#0CA3 = 03235 | - | - | - | - | Measurement parameters | R/WS | UINT (Unsigned16) | 1 s | 0 | 0 s ... 65535 s |  |  | 25
TAC2 | Time at the minimum frequency | 16#0CAA = 03242 | - | - | - | - | Measurement parameters | R/WS | UINT (Unsigned16) | 1 s | 0 | 0 s ... 65535 s |  |  | 26
FTO | Overload fault duration | 16#3857 = 14423 | - | - | - | - | Measurement parameters | R/W | UINT (Unsigned16) | 1 min | 0 | 0 min ... 6 min | (FtO) | (I_O-) (PMP-) | 27
NPL | Logic input type | 16#1003 = 04099 | - | - | - | NPL | I/O parameters | R/WS | WORD (Enumeration) | - | "POS" | - | (nPL) | (I_O-) | 28
IL1I | Logic inputs state | 16#1451 = 05201 | - | - | - | IL1I | I/O parameters | R | WORD (BitString16) | - | - | - |  |  | 29
OL1R | Logic outputs state | 16#145C = 05212 | - | - | - | OL1R | I/O parameters | R/W | WORD (BitString16) | - | - | - |  |  | 30
AI1I | Analogic input state | 16#1466 = 05222 | - | - | - | - | I/O parameters | R | INT (Signed16) | 1 | 0 | -32767 ... 32767 |  |  | 31
AI1C | Analog input 1 physical value | 16#147A = 05242 | - | - | - | - | I/O parameters | R | INT (Signed16) | Refer to programming manual | 0 | Refer to programming manual |  |  | 32
AI1R | Analog input 1 standardized value | 16#1470 = 05232 | - | - | - | - | I/O parameters | R | INT (Signed16) | 1 | 0 | -32767 ... 32767 |  |  | 33
AO1C | Analog output 1 physical value | 16#1497 = 05271 | - | - | - | - | I/O parameters | R/W | INT (Signed16) | Refer to programming manual | 0 | Refer to programming manual |  |  | 34
AO1R | Analog output 1 standardized value | 16#148D = 05261 | - | - | - | - | I/O parameters | R/W | INT (Signed16) | 1 | 0 | -32767 ... 32767 |  |  | 35
LFT | Altivar fault code | 16#1BD1 = 07121 | - | - | - | LFT | Fault parameters | R | WORD (Enumeration) | - | "NOF" | - |  |  | 36
CIC | Incorrect configuration | 16#1BDA = 07130 | - | - | - | CIC | Fault parameters | R/WS | WORD (BitString16) | - | - | - |  |  | 37
DP0 | Fault code on last fault | 16#1C20 = 07200 | - | - | - | LFT | History parameters | R | WORD (Enumeration) | - | "NOF" | - |  |  | 38
EP0 | Status word on last fault | 16#1C2A = 07210 | - | - | - | EP0 | History parameters | R | WORD (BitString16) | - | - | - |  |  | 39
DP1 | Fault code on fault n-1 | 16#1C21 = 07201 | - | - | - | LFT | History parameters | R | WORD (Enumeration) | - | "NOF" | - | (dP1) | (MAI-) | 40
ULP1 | Supply voltage on fault n-1 | 16#1C67 = 07271 | - | - | - | - | History parameters | R | UINT (Unsigned16) | 1 V | 0 | 0 V ... 65535 V |  |  | 41
LCP1 | Motor current on fault n-1 | 16#1C49 = 07241 | - | - | - | - | History parameters | R | INT (Signed16) | 0.1 A | 0 | -3276.7 A ... 3276.7 A |  |  | 42
RFP1 | Output frequency on fault n-1 | 16#1C53 = 07251 | - | - | - | - | History parameters | R | INT (Signed16) | 0.1 Hz | 0 | -3276.7 Hz ... 3276.7 Hz |  |  | 43
EP1 | Status word on fault n-1 | 16#1C2B = 07211 | - | - | - | EP0 | History parameters | R | WORD (BitString16) | - | - | - | (EP1) | (MAI-) | 44
RTP1 | Motor operating time on fault n-1 | 16#1C5D = 07261 | - | - | - | - | History parameters | R | UINT (Unsigned16) | 1 h | 0 | 0 h ... 65535 h |  |  | 45
OTP1 | Estimated Motor torque value at fault 1 | 16#1CA3 = 07331 | - | - | - | - | History parameters | R | INT (Signed16) | 1 % | 0 | -32767 % ... 32767 % |  |  | 46
TDP1 | Measured drive thermal state at fault 1 | 16#1CAD = 07341 | - | - | - | - | History parameters | R | UINT (Unsigned16) | 1 % | 0 | 0 % ... 255 % |  |  | 47
TJP1 | Estimated power component temperature (Tj) at fault 1 | 16#1CB7 = 07351 | - | - | - | - | History parameters | R | UINT (Unsigned16) | 1 °C | 0 | 0 °C ... 255 °C |  |  | 48
SFP1 | Actual motor switching frequency at fault 1 | 16#1CC1 = 07361 | - | - | - | - | History parameters | R | UINT (Unsigned16) | 1 Hz | 0 | 0 Hz ... 65535 Hz |  |  | 49
DP2 | Fault code on fault n-2 | 16#1C22 = 07202 | - | - | - | LFT | History parameters | R | WORD (Enumeration) | - | "NOF" | - | (dP2) | (MAI-) | 50
ULP2 | Supply voltage on fault n-2 | 16#1C68 = 07272 | - | - | - | - | History parameters | R | UINT (Unsigned16) | 1 V | 0 | 0 V ... 65535 V |  |  | 51
LCP2 | Motor current on fault n-2 | 16#1C4A = 07242 | - | - | - | - | History parameters | R | INT (Signed16) | 0.1 A | 0 | -3276.7 A ... 3276.7 A |  |  | 52
RFP2 | Output frequency on fault n-2 | 16#1C54 = 07252 | - | - | - | - | History parameters | R | INT (Signed16) | 0.1 Hz | 0 | -3276.7 Hz ... 3276.7 Hz |  |  | 53
EP2 | Status word on fault n-2 | 16#1C2C = 07212 | - | - | - | EP0 | History parameters | R | WORD (BitString16) | - | - | - | (EP2) | (MAI-) | 54
RTP2 | Motor operating time on fault n-2 | 16#1C5E = 07262 | - | - | - | - | History parameters | R | UINT (Unsigned16) | 1 h | 0 | 0 h ... 65535 h |  |  | 55
OTP2 | Estimated Motor torque value at fault 2 | 16#1CA4 = 07332 | - | - | - | - | History parameters | R | INT (Signed16) | 1 % | 0 | -32767 % ... 32767 % |  |  | 56
TDP2 | Measured drive thermal state at fault 2 | 16#1CAE = 07342 | - | - | - | - | History parameters | R | UINT (Unsigned16) | 1 % | 0 | 0 % ... 255 % |  |  | 57
TJP2 | Estimated power component temperature (Tj) at fault 2 | 16#1CB8 = 07352 | - | - | - | - | History parameters | R | UINT (Unsigned16) | 1 °C | 0 | 0 °C ... 255 °C |  |  | 58
SFP2 | Actual motor switching frequency at fault 2 | 16#1CC2 = 07362 | - | - | - | - | History parameters | R | UINT (Unsigned16) | 1 Hz | 0 | 0 Hz ... 65535 Hz |  |  | 59
DP3 | Fault code on fault n-3 | 16#1C23 = 07203 | - | - | - | LFT | History parameters | R | WORD (Enumeration) | - | "NOF" | - | (dP3) | (MAI-) | 60
ULP3 | Supply voltage on fault n-3 | 16#1C69 = 07273 | - | - | - | - | History parameters | R | UINT (Unsigned16) | 1 V | 0 | 0 V ... 65535 V |  |  | 61
LCP3 | Motor current on fault n-3 | 16#1C4B = 07243 | - | - | - | - | History parameters | R | INT (Signed16) | 0.1 A | 0 | -3276.7 A ... 3276.7 A |  |  | 62
RFP3 | Output frequency on fault n-3 | 16#1C55 = 07253 | - | - | - | - | History parameters | R | INT (Signed16) | 0.1 Hz | 0 | -3276.7 Hz ... 3276.7 Hz |  |  | 63
EP3 | Status word on fault n-3 | 16#1C2D = 07213 | - | - | - | EP0 | History parameters | R | WORD (BitString16) | - | - | - | (EP3) | (MAI-) | 64
RTP3 | Motor operating time on fault n-3 | 16#1C5F = 07263 | - | - | - | - | History parameters | R | UINT (Unsigned16) | 1 h | 0 | 0 h ... 65535 h |  |  | 65
OTP3 | Estimated Motor torque value at fault 3 | 16#1CA5 = 07333 | - | - | - | - | History parameters | R | INT (Signed16) | 1 % | 0 | -32767 % ... 32767 % |  |  | 66
TDP3 | Measured drive thermal state at fault 3 | 16#1CAF = 07343 | - | - | - | - | History parameters | R | UINT (Unsigned16) | 1 % | 0 | 0 % ... 255 % |  |  | 67
TJP3 | Estimated power component temperature (Tj) at fault 3 | 16#1CB9 = 07353 | - | - | - | - | History parameters | R | UINT (Unsigned16) | 1 °C | 0 | 0 °C ... 255 °C |  |  | 68
SFP3 | Actual motor switching frequency at fault 3 | 16#1CC3 = 07363 | - | - | - | - | History parameters | R | UINT (Unsigned16) | 1 Hz | 0 | 0 Hz ... 65535 Hz |  |  | 69
DP4 | Fault code on fault n-4 | 16#1C24 = 07204 | - | - | - | LFT | History parameters | R | WORD (Enumeration) | - | "NOF" | - | (dP4) | (MAI-) | 70
ULP4 | Supply voltage on fault n-4 | 16#1C6A = 07274 | - | - | - | - | History parameters | R | UINT (Unsigned16) | 1 V | 0 | 0 V ... 65535 V |  |  | 71
LCP4 | Motor current on fault n-4 | 16#1C4C = 07244 | - | - | - | - | History parameters | R | INT (Signed16) | 0.1 A | 0 | -3276.7 A ... 3276.7 A |  |  | 72
RFP4 | Output frequency on fault n-4 | 16#1C56 = 07254 | - | - | - | - | History parameters | R | INT (Signed16) | 0.1 Hz | 0 | -3276.7 Hz ... 3276.7 Hz |  |  | 73
EP4 | Status word on fault n-4 | 16#1C2E = 07214 | - | - | - | EP0 | History parameters | R | WORD (BitString16) | - | - | - | (EP4) | (MAI-) | 74
RTP4 | Motor operating time on fault n-4 | 16#1C60 = 07264 | - | - | - | - | History parameters | R | UINT (Unsigned16) | 1 h | 0 | 0 h ... 65535 h |  |  | 75
OTP4 | Estimated Motor torque value at fault 4 | 16#1CA6 = 07334 | - | - | - | - | History parameters | R | INT (Signed16) | 1 % | 0 | -32767 % ... 32767 % |  |  | 76
TDP4 | Measured drive thermal state at fault 4 | 16#1CB0 = 07344 | - | - | - | - | History parameters | R | UINT (Unsigned16) | 1 % | 0 | 0 % ... 255 % |  |  | 77
TJP4 | Estimated power component temperature (Tj) at fault 4 | 16#1CBA = 07354 | - | - | - | - | History parameters | R | UINT (Unsigned16) | 1 °C | 0 | 0 °C ... 255 °C |  |  | 78
SFP4 | Actual motor switching frequency at fault 4 | 16#1CC4 = 07364 | - | - | - | - | History parameters | R | UINT (Unsigned16) | 1 Hz | 0 | 0 Hz ... 65535 Hz |  |  | 79
NCV | Drive nominal rating | 16#0BC3 = 03011 | - | - | - | NCV | Identification parameters | R/WS | WORD (Enumeration) | - | "NO" | - | (nCU) | (MAI-) | 80
VCAL | Drive line voltage | 16#0BC4 = 03012 | - | - | - | VCAL | Identification parameters | R/WS | WORD (Enumeration) | - | "NO" | - | (UCAL) | (MAI-) | 81
INV | Nominal drive current | 16#0BC9 = 03017 | - | - | - | - | Identification parameters | R | UINT (Unsigned16) | 0.1 A | Depends of rating | 0 A ... 6553.5 A |  |  | 82
VDP | Drive software version | 16#0CE6 = 03302 | - | - | - | - | Identification parameters | R | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 83
SPN | Specific product number | 16#0CE5 = 03301 | - | - | - | - | Identification parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (SPn) | (MAI-) | 84
NC1 | Communication scanner, value of write word 1 | 16#31D9 = 12761 | - | - | - | - | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (nC1) | (OSA-) | 85
NC2 | Communication scanner, value of write word 2 | 16#31DA = 12762 | - | - | - | - | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (nC2) | (OSA-) | 86
NC3 | Communication scanner, value of write word 3 | 16#31DB = 12763 | - | - | - | - | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (nC3) | (OSA-) | 87
NC4 | Communication scanner, value of write word 4 | 16#31DC = 12764 | - | - | - | - | Communication parameters | R/W | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (nC4) | (OSA-) | 88
NM1 | Communication scanner, value of read word 1 | 16#31C5 = 12741 | - | - | - | - | Communication parameters | R | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (nM1) | (ISA-) | 89
NM2 | Communication scanner, value of read word 2 | 16#31C6 = 12742 | - | - | - | - | Communication parameters | R | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (nM2) | (ISA-) | 90
NM3 | Communication scanner, value of read word 3 | 16#31C7 = 12743 | - | - | - | - | Communication parameters | R | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (nM3) | (ISA-) | 91
NM4 | Communication scanner, value of read word 4 | 16#31C8 = 12744 | - | - | - | - | Communication parameters | R | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (nM4) | (ISA-) | 92
SCS | Save configuration | 16#1F41 = 08001 | - | - | - | SCS | Configuration management | R/WS | WORD (Enumeration) | - | "NO" | - | (SCS) | (COnF-) | 93
FCS | Restore configuration | 16#1F42 = 08002 | - | - | - | FCS | Configuration management | R/WS | WORD (Enumeration) | - | "NO" | - | (FCS) | (COnF-) | 94
CFG | Macro configuration | 16#0BEC = 03052 | - | - | - | CFG | Simply start | R/WS | WORD (Enumeration) | - | "STS" | - | (CFG) | (FULL-) | 95
LSP | Low speed | 16#0C21 = 03105 | - | - | - | - | Settings | R/W | UINT (Unsigned16) | 0.1 Hz | 0 | 0 Hz ... 400 Hz | (LSP) | (SPL-) | 96
HSP | High speed | 16#0C20 = 03104 | - | - | - | - | Settings | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0 Hz ... 400 Hz | (HSP) | (SPL-) | 97
ITH | Motor thermal current | 16#2596 = 09622 | - | - | - | - | Settings | R/W | UINT (Unsigned16) | 0.1 A | NCR | 0 A ... 6553.5 A | (ItH) | (tHt-) | 98
SFC | Speed filter coefficient ( 0(IP) to 1(PI) ) | 16#2391 = 09105 | - | - | - | - | Settings | R/W | UINT (Unsigned16) | 1 | Refer to programming manual | 0 ... 100 | (SFC) | (drC-) | 99
CTD | Motor current threshold | 16#2AF9 = 11001 | - | - | - | - | Settings | R/W | UINT (Unsigned16) | 0.1 A | INV | 0 A ... 6553.5 A | (Ctd) | (I_O-) | 100
FTD | Motor frequency threshold | 16#2AFB = 11003 | - | - | - | - | Settings | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0 Hz ... 400 Hz | (Ftd) | (I_O-) | 101
BFR | Basic frequency | 16#0BC7 = 03015 | - | - | - | BFR | Motor control | R/WS | WORD (Enumeration) | - | "50" | - | (bFr) | (drC-) | 102
NPR | Nominal Motor Power | 16#258D = 09613 | - | - | - | - | Motor control | R/WS | UINT (Unsigned16) | Refer to programming manual | Depends of rating | Refer to programming manual | (nPr) | (drC-) | 103
UNS | Nominal motor voltage | 16#2581 = 09601 | - | - | - | - | Motor control | R/WS | UINT (Unsigned16) | 1 V | 230 | 100 V ... 480 V | (UnS) | (drC-) | 104
NCR | Nominal motor current | 16#2583 = 09603 | - | - | - | - | Motor control | R/WS | UINT (Unsigned16) | 0.1 A | Depends of rating | 0 A ... 6553.5 A | (nCr) | (drC-) | 105
FRS | Nominal motor frequency | 16#2582 = 09602 | - | - | - | - | Motor control | R/WS | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 10 Hz ... 400 Hz | (FrS) | (drC-) | 106
NSP | Nominal motor speed | 16#2584 = 09604 | - | - | - | - | Motor control | R/WS | UINT (Unsigned16) | 1 rpm | Depends of rating | 0 rpm ... 24000 rpm | (nSP) | (drC-) | 107
COS | Rated motor cos Phi | 16#2586 = 09606 | - | - | - | - | Motor control | R/WS | UINT (Unsigned16) | 0.01 | Depends of rating | 0.5 ... 1 | (COS) | (drC-) | 108
MTM | Motor thermal state memo | 16#2590 = 09616 | - | - | - | N_Y | Motor control | R/WS | WORD (Enumeration) | - | "NO" | - | (MtM) | (tHt-) | 109
STUN | Autotune selection store | 16#2591 = 09617 | - | - | - | ACT | Motor control | R | WORD (Enumeration) | - | "tAb" | - |  |  | 110
FLG | Frequency loop gain | 16#2594 = 09620 | - | - | - | - | Motor control | R/W | UINT (Unsigned16) | 1 % | 20 | 0 % ... 100 % | (FLG) | (drC-) | 111
STA | Frequency loop stability | 16#2595 = 09621 | - | - | - | - | Motor control | R/W | UINT (Unsigned16) | 1 % | 20 | 0 % ... 100 % | (StA) | (drC-) | 112
TFR | Top frequency | 16#0C1F = 03103 | - | - | - | - | Motor control | R/WS | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 10 Hz ... 400 Hz | (tFr) | (drC-) | 113
TUN | Auto-tuning | 16#2588 = 09608 | - | - | - | TUN | Motor control | R/WS | WORD (Enumeration) | - | "NO" | - | (tUn) | (drC-) | 114
CTT | Motor control type assignment | 16#2587 = 09607 | - | - | - | CTT | Motor control | R/WS | WORD (Enumeration) | - | Refer to programming manual | - | (Ctt) | (drC-) | 115
UFR | IR compensation | 16#2597 = 09623 | - | - | - | - | Motor control | R/W | UINT (Unsigned16) | 1 % | 100 | 25 % ... 200 % | (UFr) | (drC-) | 116
PFL | Flux profile | 16#2598 = 09624 | - | - | - | - | Motor control | R/W | UINT (Unsigned16) | 1 % | 20 | 0 % ... 100 % | (PFL) | (drC-) | 117
SLP | Slip compensation | 16#2599 = 09625 | - | - | - | - | Motor control | R/W | UINT (Unsigned16) | 1 % | Refer to programming manual | 0 % ... 150 % | (SLP) | (drC-) | 118
SPGU | Inertia gain for the derivative term of the UF laws | 16#259D = 09629 | - | - | - | - | Motor control | R/W | UINT (Unsigned16) | 1 % | 40 | 0 % ... 1000 % |  |  | 119
RSM | Calculated (cold state) or measured stator resistance | 16#25A8 = 09640 | - | - | - | - | Motor control | R | UINT (Unsigned16) | 1 mOhm | 0 | 0 mOhm ... 65535 mOhm |  |  | 120
RSMI | Measured stator resistance | 16#25A9 = 09641 | - | - | - | - | Motor control | R | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 |  |  | 121
SFT | Switching frequency type | 16#0C1D = 03101 | - | - | - | SFT | Motor control | R/WS | WORD (Enumeration) | - | "HF1" | - | (SFt) | (drC-) | 122
SFR | Switching frequency range | 16#0C1E = 03102 | - | - | - | - | Motor control | R/W | UINT (Unsigned16) | 0.1 kHz | 40 | 2 kHz ... 16 kHz | (SFr) | (drC-) | 123
CLI | Current limitation | 16#23F1 = 09201 | - | - | - | - | Motor control | R/W | UINT (Unsigned16) | 0.1 A | Depends of rating | 0 A ... 6553.5 A | (CLI) | (CLI-) | 124
NRD | Motor noise reduction | 16#0C23 = 03107 | - | - | - | N_Y | Motor control | R/WS | WORD (Enumeration) | - | "NO" | - | (nrd) | (drC-) | 125
TCC | Type of control | 16#2B5D = 11101 | - | - | - | TCC | Inputs / outputs cfg | R/WS | WORD (Enumeration) | - | "2C" | - | (tCC) | (I_O-) | 126
TCT | 2 wire type control | 16#2B5E = 11102 | - | - | - | TCT | Inputs / outputs cfg | R/WS | WORD (Enumeration) | - | "TRN" | - | (tCt) | (I_O-) | 127
RRS | Reverse direction | 16#2B61 = 11105 | - | - | - | PSL | Inputs / outputs cfg | R/WS | WORD (Enumeration) | - | Refer to programming manual | - | (rrS) | (FUn-) | 128
AI1T | AI1 type | 16#1132 = 04402 | - | - | - | AIOT | AI1 configuration | R/WS | WORD (Enumeration) | - | Refer to programming manual | - | (AI1t) | (AI1-) | 129
CRL1 | AI1 current scaling parameter of 0% | 16#1150 = 04432 | - | - | - | - | AI1 configuration | R/WS | UINT (Unsigned16) | 0.1 mA | 40 | 0 mA ... 20 mA | (CrL1) | (AI1-) | 130
CRH1 | AI1 current scaling parameter of 100% | 16#115A = 04442 | - | - | - | - | AI1 configuration | R/WS | UINT (Unsigned16) | 0.1 mA | 200 | 0 mA ... 20 mA | (CrH1) | (AI1-) | 131
R1 | R1 assignment | 16#1389 = 05001 | - | - | - | PSL | R1 configuration | R/WS | WORD (Enumeration) | - | "FLT" | - | (r1) | (I_O-) | 132
R1S | R1 status (output active level) | 16#1069 = 04201 | - | - | - | NPL | R1 configuration | R/WS | WORD (Enumeration) | - | "POS" | - |  |  | 133
LO1 | LO1 assignment | 16#1391 = 05009 | - | - | - | PSL | LO1 configuration | R/WS | WORD (Enumeration) | - | "NO" | - | (LO1) | (LO1-) | 134
LO1S | LO1 status (output active level) | 16#1071 = 04209 | - | - | - | NPL | LO1 configuration | R/WS | WORD (Enumeration) | - | "POS" | - | (LO1S) | (LO1-) | 135
AO1 | AO1 assignment | 16#139D = 05021 | - | - | - | PSA | AO1 configuration | R/WS | WORD (Enumeration) | - | "NO" | - | (AO1) | (AO1-) | 136
AO1T | AO1 type | 16#11F9 = 04601 | - | - | - | AIOT | AO1 configuration | R/WS | WORD (Enumeration) | - | "0A" | - | (AO1t) | (AO1-) | 137
FR1 | Reference source 1 | 16#20DD = 08413 | - | - | - | PSA | Command | R/WS | WORD (Enumeration) | - | Refer to programming manual | - | (Fr1) | (CtL-) | 138
RIN | Reverse inhibition | 16#0C24 = 03108 | - | - | - | N_Y | Command | R/WS | WORD (Enumeration) | - | Refer to programming manual | - | (rIn) | (CtL-) | 139
PST | Stop key priority | 16#FA02 = 64002 | - | - | - | N_Y | Command | R/WS | WORD (Enumeration) | - | "YES" | - | (PSt) | (CtL-) | 140
CHCF | Channel configuration | 16#20D1 = 08401 | - | - | - | CHCF | Command | R/WS | WORD (Enumeration) | - | "SIM" | - | (CHCF) | (CtL-) | 141
CD1 | Channel 1 command source | 16#20E7 = 08423 | - | - | - | CDX | Command | R/WS | WORD (Enumeration) | - | "TER" | - | (Cd1) | (CtL-) | 142
RPT | Shape ramp assignment | 16#232C = 09004 | - | - | - | RPT | Ramp | R/W | WORD (Enumeration) | - | "LIN" | - | (rPt) | (rPt-) | 143
ACC | Acceleration time (between 0 and FRS) | 16#2329 = 09001 | - | - | - | - | Ramp | R/W | UINT (Unsigned16) | 0.1 s | 30 | 0 s ... 999.9 s | (ACC) | (rPt-) | 144
DEC | Deceleration time (between FRS and 0) | 16#232A = 09002 | - | - | - | - | Ramp | R/W | UINT (Unsigned16) | 0.1 s | 30 | 0 s ... 999.9 s | (dEC) | (rPt-) | 145
RPS | Ramp switch assignment | 16#2332 = 09010 | - | - | - | PSL | Ramp | R/WS | WORD (Enumeration) | - | "NO" | - | (rPS) | (rPt-) | 146
AC2 | Acceleration time 2 (between 0 and FRS) | 16#2334 = 09012 | - | - | - | - | Ramp | R/W | UINT (Unsigned16) | 0.1 s | 50 | 0 s ... 999.9 s | (AC2) | (rPt-) (PId-) | 147
DE2 | Deceleration time 2 (between FRS and 0) | 16#2335 = 09013 | - | - | - | - | Ramp | R/W | UINT (Unsigned16) | 0.1 s | 50 | 0 s ... 999.9 s | (dE2) | (rPt-) | 148
BRA | Braking function assignment | 16#232B = 09003 | - | - | - | BRA | Ramp | R/WS | WORD (Enumeration) | - | "YES" | - | (brA) | (rPt-) | 149
STT | Stop mode | 16#2BC1 = 11201 | - | - | - | STT | Stop configuration | R/WS | WORD (Enumeration) | - | "RMP" | - | (Stt) | (Stt-) | 150
NST | Free wheel stop assignment | 16#2BC2 = 11202 | - | - | - | PSL | Stop configuration | R/WS | WORD (Enumeration) | - | "NO" | - | (nSt) | (Stt-) | 151
FST | Fast stop assignment | 16#2BC4 = 11204 | - | - | - | PSL | Stop configuration | R/WS | WORD (Enumeration) | - | "NO" | - | (FSt) | (Stt-) | 152
DCF | Deceleration ramp time reduction | 16#2BDE = 11230 | - | - | - | - | Stop configuration | R/W | UINT (Unsigned16) | 1 | 4 | 1 ... 10 | (dCF) | (Stt-) | 153
ADC | Automatic DC injection | 16#28A1 = 10401 | - | - | - | ADC | Auto DC injection | R/W | WORD (Enumeration) | - | "YES" | - | (AdC) | (AdC-) | 154
SDC1 | Current level of automatic DC injection | 16#28A3 = 10403 | - | - | - | - | Auto DC injection | R/W | UINT (Unsigned16) | 0.1 A | (0,7 * NCR) | 0 A ... 6553.5 A | (SdC1) | (AdC-) | 155
TDC1 | IDC injection time | 16#28A2 = 10402 | - | - | - | - | Auto DC injection | R/W | UINT (Unsigned16) | 0.1 s | 5 | 0.1 s ... 30 s | (tdC1) | (AdC-) | 156
JOG | Jog assignment | 16#2B66 = 11110 | - | - | - | PSL | JOG | R/WS | WORD (Enumeration) | - | "NO" | - | (JOG) | (FUn-) | 157
JGF | Jog frequency | 16#2B67 = 11111 | - | - | - | - | JOG | R/W | UINT (Unsigned16) | 0.1 Hz | 50 | 0 Hz ... 10 Hz |  |  | 158
PS2 | 2 preset speeds | 16#2C89 = 11401 | - | - | - | PSL | Preset speeds | R/WS | WORD (Enumeration) | - | Refer to programming manual | - | (PS2) | (PSS-) | 159
PS4 | 4 preset speeds | 16#2C8A = 11402 | - | - | - | PSL | Preset speeds | R/WS | WORD (Enumeration) | - | Refer to programming manual | - | (PS4) | (PSS-) | 160
PS8 | 8 preset speeds | 16#2C8B = 11403 | - | - | - | PSL | Preset speeds | R/WS | WORD (Enumeration) | - | "NO" | - | (PS8) | (PSS-) | 161
SP2 | Preset speed 2 | 16#2C92 = 11410 | - | - | - | - | Preset speeds | R/W | UINT (Unsigned16) | 0.1 Hz | 100 | 0 Hz ... 400 Hz | (SP2) | (PSS-) | 162
SP3 | Preset speed 3 | 16#2C93 = 11411 | - | - | - | - | Preset speeds | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0 Hz ... 400 Hz | (SP3) | (PSS-) | 163
SP4 | Preset speed 4 | 16#2C94 = 11412 | - | - | - | - | Preset speeds | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0 Hz ... 400 Hz | (SP4) | (PSS-) | 164
SP5 | Preset speed 5 | 16#2C95 = 11413 | - | - | - | - | Preset speeds | R/W | UINT (Unsigned16) | 0.1 Hz | 250 | 0 Hz ... 400 Hz | (SP5) | (PSS-) | 165
SP6 | Preset speed 6 | 16#2C96 = 11414 | - | - | - | - | Preset speeds | R/W | UINT (Unsigned16) | 0.1 Hz | 300 | 0 Hz ... 400 Hz | (SP6) | (PSS-) | 166
SP7 | Preset speed 7 | 16#2C97 = 11415 | - | - | - | - | Preset speeds | R/W | UINT (Unsigned16) | 0.1 Hz | 350 | 0 Hz ... 400 Hz | (SP7) | (PSS-) | 167
SP8 | Preset speed 8 | 16#2C98 = 11416 | - | - | - | - | Preset speeds | R/W | UINT (Unsigned16) | 0.1 Hz | 400 | 0 Hz ... 400 Hz | (SP8) | (PSS-) | 168
JPF | Skip frequency | 16#2C25 = 11301 | - | - | - | - | Jump frequency | R/W | UINT (Unsigned16) | 0.1 Hz | 0 | 0 Hz ... 400 Hz | (JPF) | (FUn-) | 169
PIF | PID : PI function feedback assignment | 16#2E7D = 11901 | - | - | - | PSA | PID regulator | R/WS | WORD (Enumeration) | - | Refer to programming manual | - | (PIF) | (PId-) | 170
TLS | Time limited speed (LSP) | 16#2DB5 = 11701 | - | - | - | - | PID regulator | R/W | UINT (Unsigned16) | 0.1 s | 0 | [----](NO) ... 999.9 s | (tLS) | (PId-) (SPL-) | 171
FBS | PID Feedback scale factor | 16#2E7F = 11903 | - | - | - | - | PID regulator | R/W | UINT (Unsigned16) | 0.1 | 10 | 0.1 ... 100 | (FbS) | (PId-) | 172
PII | PID : PI internal reference selection | 16#2E84 = 11908 | - | - | - | N_Y | PID regulator | R/WS | WORD (Enumeration) | - | "NO" | - | (PII) | (PId-) | 173
RPI | PID : Internal reference PI | 16#2E90 = 11920 | - | - | - | - | PID regulator | R/W | UINT (Unsigned16) | 0.1 % | 0 | 0 % ... 100 % | (rPI) | (rEF-) (PId-) | 174
RPL | PID minimum value reference | 16#2E87 = 11911 | - | - | - | - | PID regulator | R/W | UINT (Unsigned16) | 0.1 % | 0 | 0 % ... 100 % | (rPL) | (PId-) | 175
RPH | PID max value reference | 16#2E88 = 11912 | - | - | - | - | PID regulator | R/W | UINT (Unsigned16) | 0.1 % | 1000 | 0 % ... 100 % | (rPH) | (PId-) | 176
RPG | PID : PI regulator proportional gain | 16#2EA5 = 11941 | - | - | - | - | PID regulator | R/W | UINT (Unsigned16) | 0.01 | 100 | 0.01 ... 100 | (rPG) | (PId-) | 177
RIG | PID : PI regulator integral gain | 16#2EA6 = 11942 | - | - | - | - | PID regulator | R/W | UINT (Unsigned16) | 0.01 | 100 | 0.01 ... 100 | (rIG) | (PId-) | 178
RDG | PID : PI regulator derivative gain | 16#2EA7 = 11943 | - | - | - | - | PID regulator | R/W | UINT (Unsigned16) | 0.01 | 0 | 0 ... 100 | (rdG) | (PId-) | 179
PRP | PID : ACC/DEC setpoint ramp parameter | 16#2ED0 = 11984 | - | - | - | - | PID regulator | R/W | UINT (Unsigned16) | 0.1 s | 0 | 0 s ... 99.9 s | (PrP) | (PId-) | 180
PIC | PID : PI regulator Reversal direction correction | 16#2EA4 = 11940 | - | - | - | N_Y | PID regulator | R/WS | WORD (Enumeration) | - | "NO" | - | (PIC) | (PId-) | 181
PAU | PID : Auto-manu | 16#2EC2 = 11970 | - | - | - | PSL | PID regulator | R/WS | WORD (Enumeration) | - | Refer to programming manual | - | (PAU) | (PId-) | 182
PIM | PID : Reference input in manual mode | 16#2EB2 = 11954 | - | - | - | PSA | PID regulator | R/WS | WORD (Enumeration) | - | "NO" | - | (PIM) | (PId-) | 183
SFS | PID predictive speed | 16#2EB3 = 11955 | - | - | - | - | PID regulator | R/WS | UINT (Unsigned16) | 0.1 Hz | 0 | [----](NO) ... 400 Hz | (SFS) | (PId-) | 184
RSL | PID : Wake up threshold on PI error | 16#2EB8 = 11960 | - | - | - | - | PID regulator | R/WS | UINT (Unsigned16) | 0.1 % | 0 | 0 % ... 100 % | (rSL) | (PId-) | 185
UPP | Wake up threshold | 16#2EBC = 11964 | - | - | - | - | PID regulator | R/W | UINT (Unsigned16) | 0.1 % | 0 | 0 % ... 100 % | (UPP) | (PId-) | 186
LFF | Withdrawal frequency | 16#1BA8 = 07080 | - | - | - | - | PID regulator | R/WS | UINT (Unsigned16) | 0.1 Hz | 0 | 0 Hz ... 400 Hz | (LFF) | (PId-) (EtF-) | 187
LPI | Reaction threshold for PI monitoring function | 16#2EBD = 11965 | - | - | - | - | PID regulator | R/W | INT (Signed16) | 0.1 % | -1 | [----](NO) ... 100 % | (LPI) | (PId-) | 188
MPI | Behaviour of PI monitoring function | 16#2EBF = 11967 | - | - | - | ECFG | PID regulator | R/WS | WORD (Enumeration) | - | "YES" | - | (MPI) | (PId-) | 189
NFD | Period for PI state point checking | 16#2ED6 = 11990 | - | - | - | - | PID regulator | R/WS | UINT (Unsigned16) | 1 min | 0 | [----](NO) ... 20 min | (nFd) | (PMP-) | 190
PR2 | PID : Assignment for 2 presets PI | 16#2E85 = 11909 | - | - | - | PSL | PID preset references | R/WS | WORD (Enumeration) | - | "NO" | - | (Pr2) | (PId-) | 191
PR4 | PID : Assignment for 4 presets PI | 16#2E86 = 11910 | - | - | - | PSL | PID preset references | R/WS | WORD (Enumeration) | - | "NO" | - | (Pr4) | (PId-) | 192
RP2 | PID : Preset PI number 2 | 16#2E91 = 11921 | - | - | - | - | PID preset references | R/W | UINT (Unsigned16) | 0.1 % | 250 | 0 % ... 100 % | (rP2) | (PId-) | 193
RP3 | PID : Preset PI number 3 | 16#2E92 = 11922 | - | - | - | - | PID preset references | R/W | UINT (Unsigned16) | 0.1 % | 500 | 0 % ... 100 % | (rP3) | (PId-) | 194
RP4 | PID : Preset PI number 4 | 16#2E93 = 11923 | - | - | - | - | PID preset references | R/W | UINT (Unsigned16) | 0.1 % | 750 | 0 % ... 100 % | (rP4) | (PId-) | 195
APO | ??? | - | - | - | - | - | - | - | - | - | - | - | - | - | -
FFD | Max speed for PI state point checking | 16#2ED7 = 11991 | - | - | - | - | Pump application | R/W | UINT (Unsigned16) | 0.1 Hz | 0 | 0 Hz ... 400 Hz | (FFd) | (PMP-) | 197
FOF | Stopping frequency of the auxiliary pump | 16#3B63 = 15203 | - | - | - | - | Pump application | R/W | UINT (Unsigned16) | 0.1 Hz | 0 | 0 Hz ... 400 Hz | (FOF) | (PMP-) | 198
FON | Starting frequency of the auxiliary pump | 16#3B62 = 15202 | - | - | - | - | Pump application | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0 Hz ... 400 Hz | (FOn) | (PMP-) | 199
FTU | Underload fault duration | 16#384D = 14413 | - | - | - | - | Pump application | R/W | UINT (Unsigned16) | 1 min | 0 | 0 min ... 6 min | (FtU) | (I_O-) (PMP-) | 200
LFD | Speed reference for PI state point checking | 16#2ED8 = 11992 | - | - | - | - | Pump application | R/W | UINT (Unsigned16) | 0.1 Hz | 0 | 0 Hz ... 400 Hz | (LFd) | (PMP-) | 201
MDE | Selecting the operating mode | 16#3B61 = 15201 | - | - | - | N_Y | Pump application | R/WS | WORD (Enumeration) | - | "NO" | - | (MdE) | (PMP-) | 202
ROF | Ramp for stopping the auxiliary pump | 16#3B67 = 15207 | - | - | - | - | Pump application | R/W | UINT (Unsigned16) | 0.1 s | 20 | 0 s ... 999.9 s | (rOF) | (PMP-) | 203
RON | Ramp for reaching the nominal speed of the auxiliary pump | 16#3B66 = 15206 | - | - | - | - | Pump application | R/W | UINT (Unsigned16) | 0.1 s | 20 | 0 s ... 999.9 s | (rOn) | (PMP-) | 204
SLE | Stop on LSP hysteresis | 16#2DB6 = 11702 | - | - | - | - | Pump application | R/W | UINT (Unsigned16) | 0.1 Hz | 10 | 0 Hz ... 400 Hz | (SLE) | (PId-) | 205
TOF | Time delay before the auxiliary pump stop command | 16#3B65 = 15205 | - | - | - | - | Pump application | R/W | UINT (Unsigned16) | 0.1 s | 20 | 0 s ... 999.9 s | (tOF) | (PMP-) | 206
TON | Time delay before starting the auxiliary pump | 16#3B64 = 15204 | - | - | - | - | Pump application | R/W | UINT (Unsigned16) | 0.1 s | 20 | 0 s ... 999.9 s | (tOn) | (PMP-) | 207
TPI | Reaction time for PI monitoring function | 16#2EBE = 11966 | - | - | - | - | Pump application | R/W | UINT (Unsigned16) | 1 s | 0 | 0 s ... 600 s | (tPI) | (PId-) | 208
INH | Fault inhibition assignment | 16#1BD5 = 07125 | - | - | - | PSL | Fault inhibition | R/WS | WORD (Enumeration) | - | "NO" | - | (InH) | (FLt-) | 209
SLL | Drive behaviour when ETIx.SLFEvent is detected on Modbus channel | 16#1B62 = 07010 | - | - | - | ECFG | Com. fault management | R/WS | WORD (Enumeration) | - | "YES" | - | (SLL) | (FLt-) | 210
LFL1 | 4-20 mA loos behaviour | 16#1B69 = 07017 | - | - | - | ECFG | Com. fault management | R/WS | WORD (Enumeration) | - | Refer to programming manual | - | (LFL1) | (FLt-) | 211
NCA1 | Communication scanner, address of write word 1 | 16#31B1 = 12721 | - | - | - | - | Communication | R/WS | UINT (Unsigned16) | 1 | 8501 | 0 ... 65535 | (nCA1) | (OCS-) | 212
NCA2 | Communication scanner, address of write word 2 | 16#31B2 = 12722 | - | - | - | - | Communication | R/WS | UINT (Unsigned16) | 1 | 8602 | 0 ... 65535 | (nCA2) | (OCS-) | 213
NCA3 | Communication scanner, address of write word 3 | 16#31B3 = 12723 | - | - | - | - | Communication | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (nCA3) | (OCS-) | 214
NCA4 | Communication scanner, address of write word 4 | 16#31B4 = 12724 | - | - | - | - | Communication | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (nCA4) | (OCS-) | 215
NMA1 | Communication scanner, address of read word 1 | 16#319D = 12701 | - | - | - | - | Communication | R/WS | UINT (Unsigned16) | 1 | 3201 | 0 ... 65535 | (nMA1) | (ICS-) | 216
NMA2 | Communication scanner, address of read word 2 | 16#319E = 12702 | - | - | - | - | Communication | R/WS | UINT (Unsigned16) | 1 | 8604 | 0 ... 65535 | (nMA2) | (ICS-) | 217
NMA3 | Communication scanner, address of read word 3 | 16#319F = 12703 | - | - | - | - | Communication | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (nMA3) | (ICS-) | 218
NMA4 | Communication scanner, address of read word 4 | 16#31A0 = 12704 | - | - | - | - | Communication | R/WS | UINT (Unsigned16) | 1 | 0 | 0 ... 65535 | (nMA4) | (ICS-) | 219
ADD | Terminal modbus : Drive address | 16#1771 = 06001 | - | - | - | - | Communication | R/WS | UINT (Unsigned16) | 1 | 0 | [----](OFF) ... 247 | (Add) | (COM-) | 220
TBR | Terminal modbus : Baud-rate | 16#1773 = 06003 | - | - | - | TBR | Communication | R/WS | WORD (Enumeration) | - | "19K2" | - | (tbr) | (COM-) | 221
TFO | Terminal modbus : Frame format | 16#1774 = 06004 | - | - | - | FOR | Communication | R/WS | WORD (Enumeration) | - | "8E1" | - | (tFO) | (COM-) | 222
TTO | Terminal modbus : Time-out | 16#1775 = 06005 | - | - | - | - | Communication | R/WS | UINT (Unsigned16) | 0.1 s | 100 | 0.1 s ... 30 s | (ttO) | (COM-) | 223
FLO | Forced local assignment | 16#20EF = 08431 | - | - | - | PSL | Communication | R/WS | WORD (Enumeration) | - | "NO" | - | (FLO) | (CtL-) | 224
FLOC | Forced local reference source assignment | 16#20F0 = 08432 | - | - | - | PSA | Communication | R/WS | WORD (Enumeration) | - | "NO" | - | (FLOC) | (CtL-) | 225
RTHI | Run elapsed time display | 16#0CA0 = 03232 | - | - | - | - | Measurement parameters | R | UINT (Unsigned16) | 0.01 h | 0 | 0 h ... 655.35 h | (rtHI) | (MAI-) | 226
PET | Process elapsed time | 16#0CA4 = 03236 | - | - | - | - | Measurement parameters | R/W | UINT (Unsigned16) | 0.01 h | 0 | 0 h ... 655.35 h | (PEt) | (MAI-) | 227
FTH | Fan time display | 16#0CA7 = 03239 | - | - | - | - | Measurement parameters | R | UINT (Unsigned16) | 0.01 h | 0 | 0 h ... 655.35 h | (FtH) | (MAI-) | 228
ULT | Application underload time delay | 16#384B = 14411 | - | - | - | - | Motor load management | R/WS | UINT (Unsigned16) | 1 s | 0 | 0 s ... 100 s | (ULt) | (I_O-) (PMP-) | 229
LUL | Application underload threshold | 16#384F = 14415 | - | - | - | - | Motor load management | R/W | UINT (Unsigned16) | 1 % | 60 | 20 % ... 100 % | (LUL) | (I_O-) (PMP-) | 230
TOL | Application Overload time delay | 16#3855 = 14421 | - | - | - | - | Motor load management | R/WS | UINT (Unsigned16) | 1 s | 0 | 0 s ... 100 s | (tOL) | (I_O-) (PMP-) | 231
LOC | Application overload threshold | 16#3859 = 14425 | - | - | - | - | Motor load management | R/W | UINT (Unsigned16) | 1 % | 90 | 70 % ... 150 % | (LOC) | (I_O-) (PMP-) | 232
SH2 | 2 HSP assignment | 16#3AFD = 15101 | - | - | - | PSL | Preset HSP | R/WS | WORD (Enumeration) | - | "NO" | - | (SH2) | (SPL-) | 233
SH4 | 4 HSP assignment | 16#3AFE = 15102 | - | - | - | PSL | Preset HSP | R/WS | WORD (Enumeration) | - | "NO" | - | (SH4) | (SPL-) | 234
HSU | Display of High speed value | 16#3B05 = 15109 | - | - | - | - | Preset HSP | R | UINT (Unsigned16) | 0.1 Hz | 0 | 0 Hz ... 400 Hz | (HSU) | (MAI-) | 235
HSP2 | High speed 2 | 16#3B06 = 15110 | - | - | - | - | Preset HSP | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0 Hz ... 400 Hz | (HSP2) | (SPL-) | 236
HSP3 | High speed 3 | 16#3B07 = 15111 | - | - | - | - | Preset HSP | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0 Hz ... 400 Hz | (HSP3) | (SPL-) | 237
HSP4 | High speed 4 | 16#3B08 = 15112 | - | - | - | - | Preset HSP | R/W | UINT (Unsigned16) | 0.1 Hz | Refer to programming manual | 0 Hz ... 400 Hz | (HSP4) | (SPL-) | 238
ETF | External fault assignment | 16#1BDB = 7131 | - | - | - | PSL | Inputs / outputs cfg | R/WS | WORD (Enumeration) | - | "NO" | - | (EtF) | (FLt-) | 239
EPL | Drive behaviour on external fault detection | 16#1B5E = 7006 | - | - | - | ECFG | Stop configuration | R/WS | WORD (Enumeration) | - | "YES" | - | (EPL) | (FLt-) | 240

## Enumerations
Code | Values | Display | Description
ACT | 0 | (tAb)
| 1 | (PEnd)
| 2 | (PrOG)
| 3 | (FAIL)
| 4 | (dOnE)
ADC | 0 | (nO)
| 1 | (YES)
| 2 | (Ct)
AIOT | 0 | (5U)
| 1 | (10U)
| 2 | (0A)
| 3 | (4A)
| 5 | (n10U)
| 6 | (GALU)
BFR | 0 | (50Hz)
| 1 | (60Hz)
BRA | 0 | (nO)
| 1 | (YES)
| 2 | (dYnA)
CDX | 1 | (tEr)
| 2 | (LOC)
| 3 | (LCC)
| 10 | (Mdb)
CFG | 0 | (StS)
| 4 | (PId)
| 9 | (SPd)
CHCF | 1 | (SIM)
| 2 | (SEP)
CTT | 0 | (PErF)
| 3 | (Std)
| 6 | (PUMP)
ECFG | 0 | (nO)
| 1 | (YES)
| 4 | (LFF)
ERRD | 16#0000 | (LFF1)
| 16#0000 | (XXXX)
| 16#0000 | (nOF)
| 16#0000 | (InF)
| 16#1000 | (OLF)
| 16#1000 | (CrF1)
| 16#1000 | (SOF)
| 16#1000 | (InFE)
| 16#2230 | (SCF4)
| 16#2310 | (OCF)
| 16#2311 | (OLC)
| 16#2320 | (SCF1)
| 16#2320 | (SCF5)
| 16#2330 | (SCF3)
| 16#3110 | (OSF)
| 16#3120 | (USF)
| 16#3130 | (PHF)
| 16#3310 | (OPF2)
| 16#3310 | (OPF1)
| 16#3310 | (ObF)
| 16#4210 | (tJF)
| 16#4210 | (OHF)
| 16#5210 | (InF9)
| 16#5210 | (InFb)
| 16#6100 | (InF1)
| 16#6100 | (InF4)
| 16#6100 | (InF3)
| 16#6100 | (InF2)
| 16#6300 | (CFI)
| 16#6300 | (CFI2)
| 16#6300 | (CFF)
| 16#7510 | (SLF1)
| 16#7510 | (SLF3)
| 16#7530 | (SLF2)
| 16#9000 | (EPF1)
| 16#FF00 | (tnF)
| 16#FF03 | (ULF)
| 16#FF04 | (SPIF)
FCS | 0 | (nO)
| 2 | (rEC1)
| 64 | (InI)
| 71 | (InI1)
FOR | 2 | (8O1)
| 3 | (8E1)
| 4 | (8n1)
| 5 | (8n2)
HMIS | 0 | (tUn)
| 1 | (dCb)
| 2 | (rdY)
| 3 | (nSt)
| 4 | (rUn)
| 5 | (ACC)
| 6 | (dEC)
| 7 | (CLI)
| 8 | (FSt)
| 11 | (nLP)
| 13 | (CtL)
| 14 | (Obr)
| 23 | (FLt)
| 24 | (FrF)
| 31 | (rEM)
| 32 | (LOC)
LFT | 0 | (nOF)
| 1 | (InF)
| 3 | (CFF)
| 4 | (CFI)
| 5 | (SLF1)
| 8 | (EPF1)
| 9 | (OCF)
| 10 | (CrF1)
| 16 | (OHF)
| 17 | (OLF)
| 18 | (ObF)
| 19 | (OSF)
| 20 | (OPF1)
| 21 | (PHF)
| 22 | (USF)
| 23 | (SCF1)
| 24 | (SOF)
| 25 | (tnF)
| 26 | (InF1)
| 27 | (InF2)
| 28 | (InF3)
| 29 | (InF4)
| 32 | (SCF3)
| 33 | (OPF2)
| 42 | (SLF2)
| 45 | (SLF3)
| 51 | (InF9)
| 53 | (InFb)
| 54 | (tJF)
| 55 | (SCF4)
| 56 | (SCF5)
| 69 | (InFE)
| 77 | (CFI2)
| 100 | (ULF)
| 101 | (OLC)
| 102 | (SPIF)
| 106 | (LFF1)
| 253 | (XXXX)
N_Y | 0 | (nO)
| 1 | (YES)
NCV | 0 | (nO)
| 1 | (U010)
| 2 | (U018)
| 3 | (U025)
| 4 | (U037)
| 5 | (U055)
| 6 | (U075)
| 7 | (U090)
| 8 | (U110)
| 9 | (U150)
| 10 | (U185)
| 11 | (U220)
| 12 | (U300)
| 13 | (U370)
| 14 | (U400)
| 15 | (U550)
| 16 | (U750)
NPL | 0 | (POS)
| 1 | (nEG)
| 2 | (EnEG)
PSA | 0 | (nO)
| 1 | (AI1)
| 129 | (OCr)
| 130 | (OFr)
| 131 | (OrP)
| 135 | (OPS)
| 136 | (OPF)
| 137 | (OPE)
| 139 | (OPr)
| 140 | (tHr)
| 141 | (tHd)
| 163 | (LCC)
| 164 | (Mdb)
| 183 | (AIU1)
PSL | 0 | (nO)
| 1 | (FLt)
| 2 | (rUn)
| 4 | (FtA)
| 5 | (FLA)
| 6 | (CtA)
| 7 | (SrA)
| 8 | (tSA)
| 10 | (PEE)
| 11 | (PFA)
| 21 | (ULA)
| 22 | (OLA)
| 123 | (AP1)
| 126 | (PMP)
| 129 | (LI1)
| 130 | (LI2)
| 131 | (LI3)
| 132 | (LI4)
| 145 | (L1L)
| 146 | (L2L)
| 147 | (L3L)
| 148 | (L4L)
RPR | 0 | (nO)
| 3 | (rtHI)
| 4 | (PtH)
| 7 | (FtH)
RPT | 0 | (LIn)
| 1 | (S)
| 2 | (U)
SCS | 0 | (nO)
| 2 | (Str1)
SFT | 1 | (HF1)
| 2 | (HF2)
STT | 0 | (rMP)
| 8 | (FSt)
| 13 | (nSt)
TBR | 24 | (4800)
| 28 | (9600)
| 32 | (19200)
| 36 | (38400)
TCC | 0 | (2C)
| 1 | (3C)
TCT | 0 | (LEL)
| 1 | (trn)
| 2 | (PFO)
TUN | 0 | (nO)
| 1 | (YES)
| 2 | (dOnE)
VCAL | 0 | (nO)
| 1 | (110M)
| 2 | (110t)
| 3 | (220M)
| 4 | (220t)

## Registers
CMD |  | bit 0: | = 1 : Switch on
|  | bit 1: | = 0 : Disable voltage
|  | bit 2: | = 0 : Quick stop/Emergency stop
|  | bit 3: | = 1 : Enable operation/Run command
|  | bit 4: | Reserved (set to 0).
|  | bit 5: | Reserved (set to 0).
|  | bit 6: | Reserved (set to 0).
|  | bit 7: | Fault reset/Fault acknowledgment active on 0 V 1 rising edge
|  | bit 8: | = 0 : RUN asked, 1 : STOP asked
|  | bit 9: | Reserved (set to 0).
|  | bit 10: | Reserved (set to 0).
|  | bit 11: | Direction of rotation command
= 0: Forward rotation
= 1: Reverse rotation. Default value, this bit can be assigned to another command.
|  | bit 12: | Reserved (set to 0).
|  | bit 13: | Reserved (set to 0).
|  | bit 14: | Reserved (set to 0).
|  | bit 15: | Reserved (set to 0).
CMI |  | bit 0: | Factory setting command (active at 1).
|  | bit 1: | Save configuration to EEPROM non-volatile memory command (active at 1).
This bit automatically changes to 0 after the request is taken into account. The command is only active if the drive is stopped, and not in "5-Operation enabled" state.
Note: If CMI is a periodic network variable, the PLC program must write it to 0 after the first request is taken into account. The life of the EEPROM memory is limited to 100,000 write operations.
Note: If the motor or configuration switching function is active, the configuration in the RAM is saved to the EEPROM in the configuration designated by [Config. Active] (CnFS).
|  | bit 2: | Reserved (= 0).
|  | bit 3: | Reserved (= 0).
|  | bit 4: | Reserved (= 0).
|  | bit 5: | Reserved (= 0).
|  | bit 6: | Reserved (= 0).
|  | bit 7: | Reserved (= 0).
|  | bit 8: | Reserved (= 0).
|  | bit 9: | Definition of the frequency reference (LFr) and output frequency (rFr) unit:
= 0 : 0.1 Hz
= 1 : Standardized value 16 signed bits based on the maximum frequency. The value 32767 corresponds to [Max frequency] (tFr). The default value of [Max frequency] (tFr) is 60 Hz, and the resolution is then approximately 0.0018 Hz.
This function has no effect on the speed reference (LFrd) or the output speed (rFrd).
|  | bit 10: | Reserved (= 0).
|  | bit 11: | Reserved (= 0).
|  | bit 12: | Reserved (= 0).
|  | bit 13: | Reserved (= 0).
|  | bit 14: | Reserved (= 0).
|  | bit 15: | Parameter consistency check
= 0: 'The check is activated. Each time a parameter is written, the drive checks the relationship between the written parameter and the configuration in the drive. For example, the [High speed] (HSP) parameter must be less than [Max frequency] (tFr).
= 1: 'The check is deactivated. The drive is locked in stop mode. In this drive state, the configuration can be written parameter by parameter and the drive does not modify the values that are written.
The switch from 1 to 0 triggers a calculation of the consistency of the configuration. Some parameters can be modified automatically by the drive.
ETA |  | bit 0: | = 1 : Ready to switch on
|  | bit 1: | = 1 : Switched on, ready
|  | bit 2: | = 1 : Operation enabled, running
|  | bit 3: | = 1 : Fault detection
|  | bit 4: | Voltage enabled (always = 1).
|  | bit 5: | = 0 : Quick stop/Emergency stop
|  | bit 6: | = 1 : Switched on disabled
|  | bit 7: | Reserved (= 0)
|  | bit 8: | Reserved (= 0)
|  | bit 9: | Remote, command or reference via the network
= 0 : Command or reference via the terminals
= 1 : Command or reference via the network
|  | bit 10: | Target reached, reference reached
= 0 : The reference is not reached
= 1 : The reference has been reached
When the drive stops, the reference has been reached.
|  | bit 11: | Internal limit active, reference outside limits
= 0 : The reference is within the limits
= 1 : The reference is not within the limits
The limits are defined by the "Low speed (LSP)" and "High speed (HSP)" parameters.
|  | bit 12: | Reserved (= 0)
|  | bit 13: | Reserved (= 0)
|  | bit 14: | Stop key, STOP via stop key
= 0 : STOP key not pressed
= 1 : Stop triggered by the STOP key on the display terminal
|  | bit 15: | Direction, direction of rotation
= 0 : Forward rotation at output
= 1 : Reverse rotation at output
ETI |  | bit 0: | = 1 : Access to the EEPROM non-volatile memory in progress
|  | bit 1: | = 0 : No parameter consistency check
= 1 : Parameter consistency check
|  | bit 2: | = 0 : The drive is not in fault state or a fault is detected
= 1 : The drive is in fault state but the fault is no longer present (not reset)
|  | bit 3: | Reserved (= 0).
|  | bit 4: | = 1 : The drive is in speed mode
|  | bit 5: | = 1 : DC injection
|  | bit 6: | = 0 : Drive in steady state
= 1 : Drive in transient state
|  | bit 7: | = 1 : Motor thermal state threshold reached for the active motor
|  | bit 8: | Reserved (= 0).
|  | bit 9: | = 1 : Acceleration in progress
|  | bit 10: | = 1 : Deceleration in progress
|  | bit 11: | = 1 : Current limit in progress
|  | bit 12: | = 1 : Fast stop in progress
|  | bit 13: | bit 13 = 0 and bit 14 = 0 : Drive controled by terminal or local keypad
|  | bit 14: | bit 13 = 1 and bit 14 = 0 : Drive controled by remote keypad
bit 13 = 0 and bit 14 = 1 : Drive controled by Modbus
bit 13 = 1 and bit 14 = 1 : Reserved
|  | bit 15: | = 0 : Forward operation applied before the ramp
= 1 : Reverse operation applied before the ramp
EP0 EP1 EP2 EP3 EP4 |  | bit 0 : | = 1 : Switched on (Same as ETA.1)
|  | bit 1 : | = 0 : Quick stop (Same as ETA.5)
|  | bit 2 : | = 1 : Switch on disabled (Same as ETA.6)
|  | bit 3 : | = 0 : Forced local mode in progress
|  | bit 4 : | = 0 : Motor rotation in forward direction (or stopped) (Same as ETA.15)
|  | bit 5 : | = 1 : Run order present (Same as ETI.4)
|  | bit 6 : | = 1 : DC injection running (Same as ETI.5)
|  | bit 7 : | = 1 : Motor thermal threshold reached (Same as ETI.7)
|  | bit 8 : | Reserved (Same as ETI.8)
|  | bit 9 : | = 1 : Product in acceleration (Same as ETI.9)
|  | bit 10 : | = 1 : Product in deceleration (Same as ETI.10)
|  | bit 11 : | = 1 : Current limit is running (Same as ETI.11)
|  | bit 12 : | = 1 : Fast stop in progress (Same as ETI.12)
|  | bit 13: | bit 13 = 0 and bit 14 = 0 : Drive controled by terminal or local keypad (Same as ETI.13 and ETI.14))
|  | bit 14: | bit 13 = 1 and bit 14 = 0 : Drive controled by remote keypad (Same as ETI.13 and ETI.14))
bit 13 = 0 and bit 14 = 1 : Drive controled by Modbus (Same as ETI.13 and ETI.14))
bit 13 = 1 and bit 14 = 1 : Reserved (Same as ETI.13 and ETI.14))
|  | bit 15: | = 1: Reverse operation applied before the ramp (Same as ETI.15)
CCC CRC |  | bit 0: | = 1: The terminal board is the active channel.
|  | bit 1: | = 1: The local keypad is the active channel.
|  | bit 2: | = 1: The remote keypad is the active channel.
|  | bit 3: | = 1: Modbus is the active channel.
|  | bit 4: | Reserved (= 0).
|  | bit 5: | Reserved (= 0).
|  | bit 6: | Reserved (= 0).
|  | bit 7: | Reserved (= 0).
|  | bit 8: | Reserved (= 0).
|  | bit 9: | Reserved (= 0).
|  | bit 10: | Reserved (= 0).
|  | bit 11: | Reserved (= 0).
|  | bit 12: | Reserved (= 0).
|  | bit 13: | Reserved (= 0).
|  | bit 14: | Reserved (= 0).
|  | bit 15: | = 1: SoMove software is the active channel.
IL1I |  | bit 0: | Value of LI1.
|  | bit 1: | Value of LI2.
|  | bit 2: | Value of LI3.
|  | bit 3: | Value of LI4.
|  | bit 4: | Reserved (= 0).
|  | bit 5: | Reserved (= 0).
|  | bit 6: | Reserved (= 0).
|  | bit 7: | Reserved (= 0).
|  | bit 8: | Reserved (= 0).
|  | bit 9: | Reserved (= 0).
|  | bit 10: | Reserved (= 0).
|  | bit 11: | Reserved (= 0).
|  | bit 12: | Reserved (= 0).
|  | bit 13: | Reserved (= 0).
|  | bit 14: | Reserved (= 0).
|  | bit 15: | Reserved (= 0).
OL1R |  | bit 0: | Value of R1.
|  | bit 1: | Reserved (= 0).
|  | bit 2: | Reserved (= 0).
|  | bit 3: | Reserved (= 0).
|  | bit 4: | Reserved (= 0).
|  | bit 5: | Reserved (= 0).
|  | bit 6: | Reserved (= 0).
|  | bit 7: | Reserved (= 0).
|  | bit 8: | Value of LO1.
|  | bit 9: | Reserved (= 0).
|  | bit 10: | Reserved (= 0).
|  | bit 11: | Reserved (= 0).
|  | bit 12: | Reserved (= 0).
|  | bit 13: | Reserved (= 0).
|  | bit 14: | Reserved (= 0).
|  | bit 15: | Reserved (= 0).
The outputs (relays or logic ouputs) can be controlled by the network. The outputs to control should not be assigned to a function of the drive, otherwise the writing is without effect.
CIC |  | bit 0: | = 1: Change of rating.
|  | bit 1: | Reserved (= 0).
|  | bit 2: | Reserved (= 0).
|  | bit 3: | = 1: Saving to the EEPROM non-volatile memory is inconsistent with power on.
|  | bit 4: | Reserved (= 0).
|  | bit 5: | Reserved (= 0).
|  | bit 6: | Reserved (= 0).
|  | bit 7: | Reserved (= 0).
|  | bit 8: | Reserved (= 0).
|  | bit 9: | Reserved (= 0).
|  | bit 10: | Reserved (= 0).
|  | bit 11: | Reserved (= 0).
|  | bit 12: | Reserved (= 0).
|  | bit 13: | Reserved (= 0).
|  | bit 14: | Reserved (= 0).
|  | bit 15: | Reserved (= 0).
If one of these events occurs, the drive will indicate a fault [Invalid config.] (CFI) and then automatically applies a factory setting.